Standard Operating Procedure

Document No. IGT_F_QA_001

|  | Prepared by | Reviewed by | Approved by |
| --- | --- | --- | --- |
| Name |  |  |  |
| Sign |  |  |  |
| Date |  |  |  |

OPGW CABLE LIVE- LINE STRINGING

PROCEDURE (SOP)

| S.L No | Description | Page no |
| --- | --- | --- |
| 1 | PURPOSE | 2 |
| 2 | SCOPE | 2 |
| 3 | REQUIRED TOOLS AND EQUIPMENT | 2 |
| 4 | SAFETY PRECAUTIONS | 3 |
| 5 | PREWORK INSPECTION | 4 |
| 6 | REQUIRED OF PPES | 4 |
| 7 | WINCH MACHINE OPERATION SYSTEM | 5 |
| 8 | PROCEDURE FOR OPGW REPLACEMENT | 6 |
| 9 | HARDWARE INSTALLATION | 8 |
| 10 | ROLE & RESPONSIBILITIES OF PERSONNEL/PARTIES INVOLVED IN ACTIVITIES | 9 |
| 11 | QUALITY CHECKPOINTS | 11 |
| 12 | EMERGENCY RESPONSE TEAM(ERT) | 12 |
| 13 | TRAINING/TBT/PTW& OTHER REFERENCE DOCUMENTS RECORDS | 12 |

1. Purpose

Provide the policies, processes, and standards needed for an organization to succeed. These help reduce errors, increase efficiency, and enhance profitability. They also create a safe work environment and provide guidelines for resolving issues and overcoming obstacles.

To define the safe and systematic procedure for removing old OPGW from transmission lines and installing new OPGW, ensuring safety, quality, and reliability.

2. Scope

The purpose of an SOP is to provide clear-cut clarification for employees and achieve consistent and excellent delivery of products and services. It ensures that team members understand and follow the standard way of working within the organization, thereby achieving consistency.

3. Required Tools & Equipment’s

| Sl. No | Description of Goods | Specification |
| --- | --- | --- |
| 1 | RACHET LEVER 1.5 T | 1.5 Ton |
| 2 | RACHET LEVER 3 T | 3 Ton |
| 3 | ROLLER 300MM | 300 MM |
| 4 | ROLLER 450MM | 450 MM |
| 5 | ROLLER 600MM | 600 MM |
| 6 | BOB ROPE | 16 MM |
| 7 | P.P ROPE 12 MM | 12MM |
| 8 | P.P ROPE 16 MM | 16MM |
| 9 | PATTA CLAMP | 5 Ton |
| 10 | WINCH MACHINE | 5 Ton |
| 11 | TRACTION MACHINE | 80 KG |
| 12 | DRUM JACK SET | 4 Ton |
| 13 | TRIPOD STAND | 5 Ton |
| 14 | RECOVERY MACHINE | As Per Required |
| 15 | EARTHING ROLLER | As Per Required |
| 16 | SWIVEL JOINT | 3 Ton |
| 17 | SINGLE END SHOCKS | 3 Ton |
| 18 | DOUBLE END SHOCKS | 3 Ton |
| 19 | RACHET LEVER 5 T | 5 Ton |
| 20 | HANGING PULLEY | As Per Required |
| 21 | DISCHARGE ROD | As Per Required |
| 22 | SAFETY SHOES | As Per Required |
| 23 | SAFETY HELMET | As Per Required |
| 24 | SAFETY JACKET | As Per Required |
| 25 | COTTON HAND GLOVES | As Per Required |
| 26 | ELECTRIC GLOVES | As Per Required |
| 27 | SAFETY BELT | As Per Required |
| 28 | FALL ARRESTER ROPE | As Per Required |
| 29 | FALL ARRESTER CLAMP | As Per Required |
| 30 | OPGW CYCLE | As Per Required |
| 31 | WALKIE TALKIE | As Per Required |
| 32 | WIRE ROPE 16 MM | 16 MM |
| 33 | WIRE ROPE 12 MM | 12 MM |
| 34 | HAND TOOLS | As Required Size |

4. SAFETY PRECAUTIONS

Hot Line Specific

- Maintain safe approach distance for the voltage level.

- Use equipotential bonding for all workers on the tower.

- Ensure correct insulation level of every tool.

- Do not use metal tools unless insulated adapters are fixed.

- No work during rain, fog, lightning, or high wind conditions.

- Clean the tower of loose metal before starting work.

- Ensure communication channels remain clear and continuous.

- Ground crew must not touch energized parts through OPGW or rope.

5. PRE-WORK INSPECTIONS

Documentation

- Work permit for live-line maintenance obtained.

- JSA & RA communicated to all concerned personnel.

- Emergency Response Plan (ERP) discussed and understood.

Tools & Equipment’s

- All hot-line tools tested for insulation.

- Rope blocks and pulleys cleaned and tested.

- OPGW drum direction verified.

- Anti-twist devices ready and available.

- Tensioner-puller alignment checked.

Site Condition

- Weather conditions checked and found suitable.

- Ground movement/restricted area verified.

- Area barricading and signage placed.

6. REQUIRED PPEs

- Safety Helmet

- Safety Shoes

- Reflective Jacket

- Cut & Impact-Resistant Gloves

- Safety Belt with Double Lanyard & Shock Absorber

- Rope Grip Fall Arrester

- Fall Arrester Clamp

- Shoulder Pad

- Retractable Fall Arrester

- Tool Kit

- Safety Net

7. Winch Machine Operation Method

A. Store and handle winches correctly.
B. Inspect the winch, rope, and accessories before use and before placing into storage.
C. Ensure mounting and suspension points are secure and suitable for the full loads that will be imposed.
D. Lift the load just clear and halt for a short period to ensure the integrity of the brake or sustaining mechanism before completing the lift.
E. Deadment shall be used to anchor the winch machine.
F. All lifting equipment should be in good condition.
G. Use a speed appropriate to the specific application.
H. Keep hands and feet clear of ropes, etc.
I. All lifting equipment’s TPI should be completed on site and       colour coded.
J. A dedicated and trained operator should be deployed at site.
K. The plan shall address the risks identified by the risk assessment, the resources required, procedures, and the responsibilities so that any lifting operation is carried out safely.
L. Stand clear of wire rope and load during operation.
M. Inspect winch installation and wire rope condition before operating the winch.
N. Operator should be medically fit.
O. Training should be provided to all workers before starting the work.
P. All loads shall be securely tied with web slings or wire rope slings to prevent roll-out during lifting.
Q. The lifting area should be barricaded and unauthorized persons shall not be allowed in the lifting area.
R. TBT (Toolbox Talk) shall be conducted daily.
S. Access shall be clear, and pre-inspection shall be completed.

8. Procedure for OPGW Replacement

8.1 Old OPGW Disconnection / Earth Wire Removal

- Disconnect clamps and hardware.

- Remove vibration dampers.

- Attach a temporary pilot rope to the old OPGW/Earth Wire.

- Maintain proper control to avoid uncontrolled fall.

Advanced Safety

- Use tag lines to control swinging.

- Monitor tension at both ends.

8.2 Pulling of Passing Pilot Rope / Messenger Rope

- Pass the pilot rope through all running blocks.

- Ensure the rope moves smoothly without twisting.

- Keep the ground crew alert to pulling direction.

8.3 Installing Winch Machine

- Place the winch machine at the receiving end.

- Establish communication links between all working teams.

- Perform pre-tension checks.

- Verify anchoring and alignment of the winch machine before operation.

8.4 OPGW Drum Preparation

- Drum direction verified.

- Swivel connector attached.

- Anti-twist device installed.

- Insulated messenger rope linked to OPGW tail.

8.5 Pulling New OPGW (Hotline Control)

- Connect OPGW to pilot rope with swivel connector.

- Start slow pulling at uniform tension.

- Check running blocks continuously.

- Maintain clear communication.

Advanced Control Measures

- Hotline workers on the tower guide OPGW using insulated guiding tools.

- Dynamometer used to prevent over-tension.

- Crew communicates using “Ready–Pull–Stop” signals.

- Use binoculars for long-span monitoring.

- Ensure no rubbing against tower steel.

- Do not exceed the allowable OPGW bending radius.

8.6 Sagging and Tensioning

- Sagging performed based on the temperature-compensated chart.

- Use digital sag measuring tools.

- Tower workers remain bonded while handling OPGW.

- Tension adjusted gradually.

Advanced

- Use laser rangefinder or sago meter for accuracy.

- Compare measured values with client specifications.

8.7 Final Hardware Installation

- Install hotline-compatible dead-end clamps.

- Fix suspension clamps using an insulated torque wrench.

- Install vibration dampers as per the client-approved spacing chart.

- Ensure proper line angle and no conductor twist.

8.9 Removal of Temporary Equipment

- Remove running blocks carefully.

- Clear all towers and ground equipment.

- Lower tools using insulated ropes.

- Remove barricading.

9. Hardware Installation

- Install hotline-compatible dead-end clamps.

- Fix suspension clamps with an insulated torque wrench.

- Install vibration dampers as per the client spacing chart.

- Ensure proper line angle and no conductor twist.

Advanced

- Use insulated platform for tension tower hardware.

- Use hot-line grade spacer/damper installation tools.

10. Roles & Responsibilities of Personnel / Parties Involved in                 Activities

Clearly define the roles and responsibilities of all personnel involved in the activity, including site management staff and subcontractor personnel such as the Project/Site Manager, Project Engineer, EHS Staff, and Competent Supervisory Staff

| Role | Accountability |
| --- | --- |
| Project Manager | Shutdown planning and approval |
| Site Engineer / In-charge | Execution and workforce coordination |
| Safety Officer | HIRA, PTW, PPE enforcement, monitoring, and HSE compliance |
| Site Supervisor | Safe dismantling operations |
| Crane / Hydra / Winch Machine Operator | Licensed and experienced personnel only |

Key Responsibilities

- Ensure earthed equipotential zones are established.

- Oversee emergency preparedness and maintain first-aid and rescue equipment.

- Hot Line Linemen / Tower Climbers

Key Responsibilities

- Perform tower-top hotline work using insulated tools only.

- Install and remove hotline running blocks, sheaves, and pulleys.

- Maintain equipotential bonding while working near energized parts.

- Attach pilot rope, guide OPGW, and install hardware safely.

- Communicate hazards, clearance issues, or abnormal conditions immediately.

- Follow instructions from the Hot Line Supervisor and maintain disciplined movement.

Ground Crew Team- Responsibilities

- Operate ground pulling equipment and assist in rope management.

- Maintain proper alignment of pilot rope and OPGW.

- Avoid contact between rope/OPGW and grounded objects.

- Assist in tool lifting/lowering, drum handling, and hardware preparation.

- Maintain barricades and ensure public safety around work zones.

- Support communication between tower crews and machine operators.

- Winch Machine Operators

Key Responsibilities

- Inspect and calibrate machines before operation.

- Maintain uniform pulling and tensioning as per supervisor instructions.

- Use hot-line-rated insulating links between machine and rope.

- Respond immediately to STOP/EMERGENCY commands.

- Avoid sudden jerks or over-tension that can damage OPGW.

- Record tension readings, pulling force, and sagging parameters.

11. QUALITY CHECKPOINTS

- No twist or damage in OPGW.

- Sag and tension values are within specification.

- All hardware torqued to the correct value.

- Dampers installed at exact specified locations.

- Insulating tools marked “Tested OK”.

- No foreign objects left on the tower.

12. Emergency Response Team (ERT)

Key Responsibilities

- Maintain standby readiness during hotline work.

- Provide rapid rescue support in case of fall, shock, or arc incidents.

- Coordinate with the nearest hospital or ambulance service.

- Maintain hotline rescue kits and fall recovery equipment.

- Ensure a dedicated emergency vehicle is available at the work site.

13. Training / TBT / PTW & Other Reference Documents Records

A training record is a systematic collection of data and information that documents an individual's or group's training history, including the type, duration, and outcome of training activities, assessments, and evaluations.

- Work Permit System

- HIRA / JSA for Tower Dismantling

- PPE Standards (IS:15298 / EN Standards)

- Safety Training Records

- Toolbox Talk (TBT) Records

- Permit to Work (PTW) Records

- Emergency Response Plan (ERP) Records

- Equipment Inspection and Test Certificates

- Hot-Line Tools Testing & Certification Records

- Medical Fitness Certificates of Workers

- Operator Competency and License Records

- Daily Site Inspection Checklists

- Incident / Near-Miss Reporting Records

- Client Specifications and Approved Method Statements

- Relevant Applicable Standards and Procedures